Revised March 18, 2026

Cable Sensors (01CT & 22CT)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Sensors shall be NEMA 4X/IP65 or IP67 rated.  Those with a housing shall incorporate a screwless snap-on cover with a detachable mounting plate.

- Sensors shall be cULus listed and manufactured under ISO 9001 International Quality Control Standards.

- Note to Specifier:  Choose Ambient Temperature & Operating Temperature ranges to meet the requirements of the design.  Ensure the selected temperatures are identical.

- Ambient temperature:

  - Passive: [-40oF to +300oF (-40oC to +150oC)] or [-13oF to +167oF (-25oC to +175oC)]

  - Active: -30oF to +120oF (-35oC to +50oC)

- Operating temperature:

- Passive: [-40oF to +300oF (-40oC to +150oC)] or [-13oF to +167oF (-25oC to +175oC)]

- Active: -60oF to +320oF (-50 oC to +160 oC)

- Accuracy:

- Passive: NTC (Thermistor)  +/-0.35 oF @ 77 oF (+/-0.2oC @ 25oC); Platinum (Pt) +/-0.5 oF @ 32 oF (+/-0.3oC @ 0oC); Nickel (Ni) +/-0.7 oF @ 32 oF (+/-0.4oC @ 0oC)

- Active: +/- 1% of the selected measuring range

- Power Supply (Active): DC 15-24V (+/- 10%), AC 24V (+/-10%)

- Outputs:

- Passive:  Resistance.

- Active: Voltage 0-5 or 0-10 VDC.