Revised March 25, 2026

Section 280900 Duct (Air) Sensors

Duct and Pipe (Temperature) Sensors (01DT & 22DT)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Sensors with housing shall incorporate a screwless snap-on cover with a detachable mounting plate and NEMA 4X/IP65 rating with a stainless steel probe.

- Note to Specifier:  Insert the following statement for pipe (liquid) applications, choosing the appropriate material.

- A [stainless steel] [brass] thermowell shall be required for all liquid applications.

- Sensors shall be cULus listed and manufactured under ISO 9001 International Quality Control Standards.

- Ambient temperature:

  - Passive: : -40oF to +300oF (-40oC to +150oC)

  - Active: -30oF to +120oF (-35oC to +50oC)

- Operating temperature:

  - Passive: NTC (Thermistor)  -60oF to +300oF (-50oC to +150oC); Platinum (Pt), Nickel (Ni) -60oF to +320oF (-50oC +160oC)

  - Active: -60oF to +320oF (-50 oC to +160 oC)

- Accuracy:

  - Passive: NTC (Thermistor)  +/-0.35 oF @ 77 oF (+/-0.2oC @ 25oC); Platinum (Pt) +/-0.5 oF @ 32 oF (+/-0.3oC @ 0oC); Nickel (Ni) +/-0.7 oF @ 32 oF (+/-0.4oC @ 0oC)

  - Active: +/- 1% of the selected measuring range

- Power Supply (Active): DC 15-24V (+/- 10%), AC 24V (+/-10%)

- Outputs:

  - Passive:  Resistance.

  - Active: Voltage 0-5 or 0-10 VDC.