Revised March 18, 2026

Low Limit Detection Sensors (01DTS)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Sensors shall be NEMA 4/IP65 rated.

- Sensors shall be manufactured under ISO 9001 International Quality Control Standards.

- Ambient temperature: -30oF to +160oF (-35oC to +70oC)

- Fluid temperature: -30oF to +160oF (-35oC to +70oC)

- Setpoint range: 15oF to 60oF (-10oC to +15oC)

- Accuracy: +/-0.9 oF (+/-0.5oC)

- Outputs: 1xSPDT (4A @ AC/DC 24V)

- Note to Specifier:  Choose reset option to meet the requirements of the design.

- [Manual] [Auto] reset

- Probe shall be mounted in a serpentine manner to provide adequate coverage with a manufacturer supplied mounting kit utilized to mount the element.