Revised March 18, 2026

Duct (Averaging Temperature) Sensors (01MT & 22MT)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Housing shall incorporate a screwless snap-on cover with a detachable mounting plate and NEMA 4X/IP65 rating.

- Sensors shall be cULus listed and manufactured under ISO 9001 International Quality Control Standards.

- Ambient temperature: -30oF to +120oF (-35oC to +50oC)

- Operating temperature:

  - Passive: NTC (Thermistor)  -60oF to +300oF (-50 oC to +150 oC); Platinum (Pt), Nickel (Ni)

- -60oF to +320oF (-50 oC to +160 oC)

  - Active: -30oF to +160oF (0 oC to +70 oC)

- Accuracy:

  - Passive: NTC (Thermistor)  +/-0.35 oF @ 77 oF (+/-0.2oC @ 25oC); Platinum (Pt)  +/-0.5 oF @ 32 oF (+/-0.3oC @ 0oC); Nickel (Ni)  +/-0.7 oF @ 32 oF (+/-0.4oC @ 0oC)

  - Active: +/- 1% of the selected measuring range

- Power Supply (Active): DC 15-24V (+/- 10%), AC 24V (+/-10%)

- Outputs:

  - Passive:  Resistance.

  - Active: Voltage 0-5 or 0-10 VDC.

- Averaging elements shall be available in 10ft (3m), 20ft (6m) or 50ft (15m) lengths to provide adequate coverage of the measured airstream mounted in a serpentine manner.  Averaging sensors shall incorporate multi-point elements. True averaging sensors consisting of one continuous RTD across the entire length of the probe.

- A manufacturer supplied duct mounting kit should be utilized to mount the averaging element.