Revised March 18, 2026

Duct (Air Quality) Sensors (22DC, 22DTC, 22DTM, 22DCV, 22DCK, 22DCM)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Housing shall incorporate a screwless snap-on cover with a detachable mounting plate and NEMA 4X/IP65 rating.

- Sensors shall be cULus listed and manufactured under ISO 9001 International Quality Control Standards.

- Ambient temperature: 32oF to 122oF (0oC to 50oC)

- Operating temperature: 32oF to 122oF (0oC to 50oC)

- Accuracy:

  - Temperature: +/-0.9 oF @ 70 oF (+/-0.5oC @ 21oC)

  - Humidity: +/-2% between 10 and 90% RH @ 70 oF (21oC)

  - CO2: +/-(50ppm +3% of reading)

- Power Supply: DC 15-24V (+/- 10%), AC 24V (+/-10%)

- Note to Specifier:  Choose the appropriate measured values to meet the requirements of the design.

- Measured values shall include [CO2], [Temperature], [Humidity], [VOC], [Mix CO2+VOC]

- Humidity element shall be a polymer-based capacitive sensor with stainless steel wire mesh filter.

- Optional CO2/Humidity/Temperature with BACnet MS/TP.