Revised March 18, 2026

Duct (Combination Temperature/Humidity) Sensors (22DTH)

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Housing shall incorporate a screwless snap-on cover with a detachable mounting plate and NEMA 4X/IP65 rating.

- Measured values shall include temperature and selectable from relative humidity, absolute humidity, dew point, or enthalpy.

- Sensors shall be cULus listed and manufactured under ISO 9001 International Quality Control Standards.

- Ambient temperature: -30oF to +120oF (-35oC to +50oC)

- Operating temperature: -30oF to +120oF (-35oC to +50oC)

- Accuracy:

  - Passive: NTC (Thermistor) +/-0.35 oF @ 77 oF (+/-0.2oC @ 25oC); Platinum (Pt) +/-0.5 oF @ 32 oF (+/-0.3oC @ 0oC); Nickel (Ni) +/-0.7 oF @ 32 oF (+/-0.4oC @ 0oC)

  - Active: +/- 0.54 oF @ 77 oF (+/-0.3oC @ 25oC)

  - Humidity: +/-2% between 0 and 80% RH @ 77 oF (25oC)

- Power Supply: DC 15-24V (+/- 10%), AC 24V (+/-10%)

- Outputs:  0-5 VDC/0-10 VDC or 4-20mA.

- Humidity element shall be a polymer-based capacitive sensor with stainless steel wire mesh filter.

- BACnet MS/TP and ModBus RTU shall be available as required with all measured values reported.