Revised July 22, 2025

Section 230900 Control Valves

3-way Diverting Industrial Ball Valves (Belimo L-Series)

- The control valve and actuator assembly shall be provided and delivered from a single manufacturer.

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 2 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Where indicated, provide actuator to fail to an end position.

- Actuators shall be protected from overload at all angles of rotation.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water; 150% steam design pressure.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be nickel plated (forged) brass.  Chrome plated brass ball and nickel plated brass stem with PTFE.

- Media water temperature shall be 0oF to 250oF (-18oC to +120oC) with maximum 60% glycol solution.

- Valve shall be a diverting/changeover switching flow pattern with a modified linear characteristic with 0% Leakage.