Revised July 22, 2025

Section 230900 Control Valves

6-way Valve (Belimo Characterized Control Valves)

- The control valve and actuator assembly shall be provided and delivered from a sing le manufacturer.

- Manufactured, brand labeled or distributed by Belimo.

- The manufacturer shall warrant all components for a period of 5 years from the date of production.

- Actuators for valves shall be cULus listed and be manufactured under ISO 9001 International Quality Control Standards.

- Actuator shall be provided with a means of manual override upon power loss.

- Actuators shall be protected from overload at all angles of rotation.

- Control valve and actuator assembly shall be capable of closing valve against 150% system pump shutoff head for water; 150% steam design pressure.  3-way mixing valves shall be capable of closing valve against 150% of system differential pressure.

- Control valve bodies shall be nickel plated (forged) brass.  Chrome plated brass ball and blow-out proof stem with PTFE and double EPDM O-Rings.  Valve body shall incorporate chrome plated steel characterizing discs.

- Media water temperature shall be 43oF to 180oF (6oC to 82oC) with maximum 60% glycol solution.

- Valve (A-AB) shall be linear flow characteristic with 0% Leakage.

- The valve shall incorporate a loop pressure relief to release any pressure build up in the loop when the valve is in the isolated position.

Note to Specifier:  To incorporate a condensate sensor add the following statement.

- Incorporate a condensate sensor with LED indication to close the valve upon sensing condensate.