Revised November April 29th, 2024

SECTION 233300 – AIR DUCT ACCESSORIES

      - SMOKE DAMPERS

        - Damper Motors: [Proportional] [or] [two-position] action.

          - Manufactured, brand labeled or distributed by Belimo.

          - Voltage:  Two-position actuators shall be [24 VAC] [120 VAC].  Proportional actuators shall be 24 VAC.

Agency Listings:

UL 873 or UL 60730, UL 2043, ISO 9001.

[<NYC Office of Technical Certification and Research> <local standard> where required.]

          - New construction damper actuators shall be provided by the damper manufacturer

#### per UL 555S requirements.

          - Coupling:  V-bolt dual nut clamp with a V-shaped toothed cradle.  Aluminum clamps or setscrews are not acceptable.

          - Overload Protection:  Microprocessor or an electronic based motor controller providing burnout protection if stalled before full rotation is reached.  The actuator shall electronically cut off at full open to eliminate noise generation.

          - Temperature rating:  Actuator shall have UL 555S listings by the damper manufacturer for [250 DegF (121 DegC)] [350 DegF (176 DegC)].

          - Proportional Smoke Damper Actuators shall meet all requirements specified above and shall modulate 0-100% open in response to a 2-10vdc control signal.   A 2-10vdc feedback output shall be available for position indication. A manual override winder and locking mechanism shall be provided for operation upon loss of power.

          - The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

        - Accessories:

          - [Integral auxiliary switches] [damper blade switches] shall be provided on all actuators as required.

          - Testing Devices

[A [momentary] [keyed] test switch with open and closed position indication lights shall be provided [where indicated].

[BACnet Remote Damper Testing Module shall be provided to initiate testing by a single BACnet command.  Results, pass or fail, shall be communicated to the BACnet controller via BACnet MS/TP RS 485 network communication.  The remote testing module shall be UL 60730 listed.]

      - COMBINATION FIRE AND SMOKE DAMPERS

        - Damper Motors: [Proportional] [or] [two-position] action.

          - Manufactured, brand labeled or distributed by Belimo.

          - Voltage:  Two-position actuators shall be [24 VAC] [120 VAC].  Proportional actuators shall be 24 VAC.

Agency Listings:

UL 873 or UL 60730, UL 2043 ISO 9001.

[<NYC Office of Technical Certification and Research> <local standard> listed where required.]

          - New construction damper actuators shall be provided by the damper manufacturer per UL 555 and UL 555S requirements.

          - Coupling:  V-bolt dual nut clamp with a V-shaped toothed cradle.  Aluminum clamps or setscrews are not acceptable.

          - Overload Protection:  Microprocessor or an electronic based motor controller providing burnout protection if stalled before full rotation is reached.  The actuator shall electronically cut off at full open to eliminate noise generation.

          - Temperature rating:  Actuator shall have UL 555S listings by the damper manufacturer for [250 DegF (121 DegC)] [350 DegF (176 DegC)].

          - Proportional Smoke Damper Actuators shall meet all requirements specified above and shall modulate 0-100% open in response to a 2-10vdc control signal.   A 2-10vdc feedback output shall be available for position indication. A manual override winder and locking mechanism shall be provided for operation upon loss of power.

          - The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

        - Accessories:

          - [Integral auxiliary switches] [damper blade switches] shall be provided on all actuators as required.

          - Testing Devices

[A [momentary] [keyed] test switch with open and closed position indication lights shall be provided [where indicated].

[BACnet Remote Damper Testing Module shall be provided to initiate testing by a single BACnet command.  Results, pass or fail, shall be communicated to the BACnet controller via BACnet MS/TP RS 485 network communication.  The remote testing module shall be UL 60730 listed.]

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.