GAS DETECTION MONITORING SYSTEM

  - The manufacturer shall warrant all components (except sensing element) for a period of 5 years from the date of delivery.

  - Manufactured, brand labeled or distributed by Belimo.

  - All sensing elements must be capable of field calibration or field replacement with a factory calibrated sensing element.

  - Sensing elements shall be mounted per the manufacturer’s recommended height.

  - Carbon Monoxide

    - Element Type:  Electrochemical

    - Ranges:

      - Measurement:	0-250 ppm full scale

      - Detection Range:  15 m radius

      - Operating Temperature:	-20 to 40 ℃

      - Humidity:

        - 15-90% rH continuous

        - 0-99% rH intermittent, non-condensing

    - Performance:

      - Accuracy: ±3% full scale (0-75 ppm)

      - Drift:	<5% (annual)

      - Repeatability:  <+3%

      - Response Time:  <30 seconds (T90)

  - Nitrogen Dioxide

    - Element Type:  Electrochemical

    - Ranges:

      - Measurement:  0-10 ppm full scale

      - Detection Range:  15 m radius

      - Operating Temperature:  -20 to 40 ℃

      - Humidity:

        - 15-90% rH maximum continuous

        - 0-99% rH intermittent, non-condensing

    - Performance:

      - Accuracy: -0.1 to + 6.5% full scale (0-2 ppm)

      - Drift:	<+2% (monthly)

      - Repeatability:  <+2%

      - Response Time:  <30 seconds (T90)

  - Power Supply:

    - Voltage:	AC/DC 24V

    - Frequency:	50/60 Hz

    - Apparent Power:  5VA (210 mA)

  - Outputs:

    - Type A

        - Binary:	(1) SPDT 5A @ 125VAC relay

        - Analog:	(2), 4-20mA or 2-10 VDC

    - Type B

        - Binary:	(2) SPDT 5A@ 125VAC relays

  - User Interface

    - Backlit LCD display of gas concentration, user settings and calibration controls.

    - LED alarm indicators for 3 levels of alarm:  Red for gas level 1 and 2; high intensity white strobe for gas level 3.

    - Audible alarm, 80db at 1 meter.

  - Agency Listings:

    - UL 2075 assemblies for CO single, NO2 single, and CO/NO2 dual monitors; CSA C22.2.No. 61010-1-12, UL94 5VA enclosure.

  - Communication:

    - CAN network operation as addressable nodes.

    - BTL listed BACnet MS/TP RS485 for integration to the building automation system.